## Sheet1
| State | Condensor outlet | Evaporator inlet | accumulator intlet/evaporator outlet | accumulator outlet/compressor inlet | compressor outlet | condensor inlet | evaporator T | Ambient | Condensor T | Flow meter outlet | Evaporator inlet | Compressor Inlet | Condensor inlet/compressor outlet
|  | T: degrees C | [8 empty] | PSI |  | gage pressures - add offset |  |  | evaporative | compressor | condenser | observations
|  | T1 | T2 | T3 | T4 | T5 | T6 | T7 | T8 | T10 | P1 | P2 | P3 (suction) | P4 | mdot | A1 | A2 | A3
First Condition | Pressure Controlled Expander | 23.2 | -31.4 | 20 | 19.8 | 25.4 | 23.2 | 21 | 18.4 | 22.6 | 80 | 11.5 | 2 | 95 | 0.285 | 0.572 | 5.47 | 0.558 | both condensor and evaporator air feel cold
Second Condition |  | 27.2 | -19.8 | 19.6 | 20.2 | 44 | 35.6 | 20.2 | 18.8 | 25.4 | 102 | 20 | 7 | 110 | 0.45 | 0.567 | 5.8 | 0.552 | frost covered pipes - evaporator inlet? |  | 6.8948
Third Condition |  | 33.6 | -8.4 | 17.4 | 19.8 | 61.6 | 53.8 | 14.6 | 18.6 | 29.2 | 125 | 31.5 | 15 | 132 | 0.75 | 0.565 | 6.42 | 0.55
Fourth Condition |  | 43.2 | 4 | 2.4 | 4.8 | 74.2 | 68 | 11.8 | 18.6 | 35.6 | 165 | 51 | 30 | 174 | 1.25 | 0.562 | 7.7 | 0.547 | frost melted; reverse condensation | P1 (kPa) | P2 (kPa)
Both high | Thermally- controlled expander | 41.8 | 2.2 | 12 | 11 | 75.8 | 70.6 | 11.6 | 18.6 | 34.6 | 157 | 48 | 27.5 | 167 | 1.2 | 0.562 | 7.44 | 0.547 |  | 1103.1616 | 337.8432
condensor fan low |  | 45.8 | 2.6 | 11.8 | 14 | 78.8 | 73.2 | 11.6 | 18.8 | 39.2 | 175 | 48.5 | 28.5 | 185 | 1.2 | 0.562 | 7.64 | 0.36 |  | 1310.0044 | 358.5275
both high | Capillary Tube expander - both high | 42 | 14.2 | 9.4 | 17.8 | 84.6 | 77.8 | 11.4 | 18.8 | 35 | 160 | 49 | 29.5 | 170 | 1.2 | 0.562 | 7.57 | 0.547 | initially bubbles in observer; T unstable | 1116.9511 | 324.0537
evaporator high, condensor low |  | 49.2 | 18.4 | 4 | 7.2 | 88.6 | 81.6 | 12.4 | 18.8 | 41.4 | 190 | 52 | 32.5 | 200 | 1.3 | 0.561 | 8.1 | 0.362
evaporator low, condensor high |  | 43.2 | 17 | 1 | 5.4 | 89.2 | 81.6 | 8.8 | 19.2 | 35.2 | 162 | 47 | 28.5 | 171 | 1.15 | 0.372 | 7.49 | 0.548 | bubbles